## LR Incremental Costs
|  |  |  | NZ | UNI | LNI | USI | LSI
|  |  | Capital cost increment ($m) | 1824.9713 | 906.4449 | 387.39 | 381.0613 | 150.0752
|  |  | Cost increment ($m), with incremental opex @ 2.2% | 1865.1206 | 926.3866 | 395.9125 | 389.4446 | 153.3768
|  |  | Demand increment (MW) | 2221 | 1017.4 | 552.7 | 748.8 | 165
|  |  | Long-run average incremental cost ($/MW) | 839766.1518 | 910543.1893 | 716324.466 | 520091.625 | 929556.6136
|  |  | Long-run marginal incremental cost ($/MW) | 47533.9331 | 51540.1805 | 40546.6679 | 29439.1486 | 52616.4121
|  |  | Present value (discount rate 6%) | NZ | UNI | LNI | USI | LSI
|  | PV | Capital cost increment ($m) | 777.6314 | 382.7958 | 146.3809 | 183.4306 | 65.024
|  |  | Cost increment ($m), with incremental opex @ 2.2% | 794.7392 | 391.2173 | 149.6013 | 187.4661 | 66.4545
|  |  | Demand increment (MW) | 947.7509 | 433.7921 | 238.5793 | 313.0296 | 72.3196
|  |  | Long-run average incremental cost ($/MW) | 838552.8761 | 901854.3201 | 627050.5824 | 598876.7286 | 918900.2804
|  |  | Long-run marginal incremental cost ($/MW) | 47465.2571 | 51048.3577 | 35493.4292 | 33898.6827 | 52013.2234
|  | National incremental transmission costs with peak demand drivers ($m and MW) | [9 empty] | Regional allocations (transmission pricing regions) ($m and MW)
|  | E&D base capex | Major and listed capex (including non E&D) | Major and listed capex - E&D component | Total cost | PV cost | Demand | Demand change | Demand growth | PV demand | PV demand change | E&D base capex |  |  |  | Major and listed capex E&D |  |  |  | Total cost |  |  |  | PV cost |  |  |  | Demand |  |  |  | Demand change |  |  |  | PV demand |  |  |  | PV demand change
RCP | Year | NZ | NZ | NZ | NZ | NZ | NZ | NZ | NZ | NZ | NZ | UNI | LNI | USI | LSI | UNI | LNI | USI | LSI | UNI | LNI | USI | LSI | UNI | LNI | USI | LSI | UNI | LNI | USI | LSI | UNI | LNI | USI | LSI | UNI | LNI | USI | LSI | UNI | LNI | USI | LSI
2 | 2016 | 9.0003 |  |  | 9.0003 | [6 empty] | E&D base capex UNI: 3.2531; E&D base capex LNI: 0.87729; E&D base capex USI: 4.1169; E&D base capex LSI: 0.75307; Total cost UNI: 3.2531; Total cost LNI: 0.87729; Total cost USI: 4.1169; Total cost LSI: 0.75307
2 | 2017 | 21.0612 |  |  | 21.0612 | [6 empty] | E&D base capex UNI: 9.432; E&D base capex LNI: 8.0475; E&D base capex USI: 0.73199; E&D base capex LSI: 2.8496; Total cost UNI: 9.432; Total cost LNI: 8.0475; Total cost USI: 0.73199; Total cost LSI: 2.8496
2 | 2018 | 34.4004 |  |  | 34.4004 | [6 empty] | E&D base capex UNI: 10.8793; E&D base capex LNI: 16.5855; E&D base capex USI: 1.5516; E&D base capex LSI: 5.3839; Total cost UNI: 10.8793; Total cost LNI: 16.5855; Total cost USI: 1.5516; Total cost LSI: 5.3839
2 | 2019 | 21.578 |  |  | 21.578 | [6 empty] | E&D base capex UNI: 13.8009; E&D base capex LNI: 2.5923; E&D base capex USI: 2.5923; E&D base capex LSI: 2.5923; Total cost UNI: 13.8009; Total cost LNI: 2.5923; Total cost USI: 2.5923; Total cost LSI: 2.5923
2 | 2020 | 9.0604 |  |  | 9.0604 | 8.5476 | 6616 |  |  | 6241.5094 |  | 3.119 | 1.1406 | 3.6603 | 1.1406 |  |  |  |  | 3.119 | 1.1406 | 3.6603 | 1.1406 | 2.9425 | 1.076 | 3.4531 | 1.076 | 2821.7 | 1911.6 | 1358.9 | 1037.1 |  |  |  |  | 2661.9811 | 1803.3962 | 1281.9811 | 978.3962
3 | 2021 | 15.3 | 29.8313 | 23.9612 | 39.2612 | 34.9424 | 6691 | 75 | 1.134% | 5954.9662 | 66.7497 | 5.9912 | 4.27 | 2.1028 | 2.9359 | 23.8213 | 0.046658 | 0.046658 | 0.046658 | 29.8125 | 4.3167 | 2.1495 | 2.9826 | 26.533 | 3.8418 | 1.913 | 2.6545 | 2854.1 | 1929.4 | 1378.4 | 1042.8 | 32.4 | 17.8 | 19.5 | 5.7 | 2540.1388 | 1717.1591 | 1226.7711 | 928.0883 | 28.8359 | 15.8419 | 17.3549 | 5.073
3 | 2022 | 15.3 | 77.1288 | 66.7697 | 82.0697 | 68.9073 | 6759 | 68 | 1.016% | 5674.9867 | 57.0941 | 5.9912 | 4.27 | 2.1028 | 2.9359 | 66.5205 | 0.083072 | 0.083072 | 0.083072 | 72.5117 | 4.3531 | 2.1859 | 3.019 | 60.8822 | 3.6549 | 1.8353 | 2.5348 | 2885.9 | 1948 | 1397.4 | 1048.6 | 31.8 | 18.6 | 19 | 5.8 | 2423.0573 | 1635.5784 | 1173.284 | 880.4248 | 26.6999 | 15.6169 | 15.9528 | 4.8698
3 | 2023 | 15.3 | 58.5174 | 30.7632 | 46.0632 | 36.4864 | 6831 | 72 | 1.065% | 5410.7918 | 57.0307 | 5.9912 | 4.27 | 2.1028 | 2.9359 | 19.9508 | 0.0067565 | 10.7989 | 0.0067565 | 25.942 | 4.2768 | 12.9018 | 2.9427 | 20.5485 | 3.3876 | 10.2194 | 2.3309 | 2917 | 1968 | 1418.2 | 1055.3 | 31.1 | 20 | 20.8 | 6.7 | 2310.5372 | 1558.8403 | 1123.3472 | 835.8964 | 24.6341 | 15.8419 | 16.4755 | 5.307
3 | 2024 | 15.3 | 110.8303 | 40.5197 | 55.8197 | 41.7117 | 6901 | 70 | 1.025% | 5156.8287 | 52.3081 | 5.9912 | 4.27 | 2.1028 | 2.9359 | 4.8147 | 0.60455 | 35.0936 | 0.0069044 | 10.8059 | 4.8746 | 37.1964 | 2.9428 | 8.0748 | 3.6426 | 27.7953 | 2.1991 | 2949.1 | 1985.9 | 1438.9 | 1061.1 | 32.1 | 17.9 | 20.7 | 5.8 | 2203.7391 | 1483.98 | 1075.2298 | 792.9156 | 23.987 | 13.3759 | 15.4682 | 4.3341
3 | 2025 | 17.8 | 37.2181 | 26.0767 | 43.8767 | 30.9313 | 6972 | 71 | 1.029% | 4914.9849 | 50.0522 | 6.9702 | 4.9677 | 2.4464 | 3.4156 | 0.0071045 | 1.5185 | 24.5439 | 0.0071045 | 6.9773 | 6.4863 | 26.9904 | 3.4228 | 4.9187 | 4.5726 | 19.0272 | 2.4129 | 2981.9 | 2004.1 | 1464.3 | 1066.4 | 32.8 | 18.2 | 25.4 | 5.3 | 2102.1218 | 1412.8114 | 1032.2737 | 751.7699 | 23.1227 | 12.8303 | 17.906 | 3.7363
4 | 2026 | 17.9 | 52.5875 | 6.3072 | 24.2072 | 16.0992 | 7045 | 73 | 1.047% | 4685.3274 | 48.5492 | 7.0093 | 4.9957 | 2.4602 | 3.4348 | 1.5768 | 1.5768 | 1.5768 | 1.5768 | 8.5861 | 6.5725 | 4.037 | 5.0116 | 5.7103 | 4.3711 | 2.6848 | 3.333 | 3015.3 | 2022.6 | 1489.7 | 1072.7 | 33.4 | 18.5 | 25.4 | 6.3 | 2005.3467 | 1345.1445 | 990.7356 | 713.4068 | 22.2129 | 12.3036 | 16.8925 | 4.1899
4 | 2027 | 18 | 52.5892 | 6.3074 | 24.3074 | 15.2507 | 7114 | 69 | 0.9794% | 4463.4116 | 43.2915 | 7.0485 | 5.0236 | 2.4739 | 3.454 | 1.5768 | 1.5768 | 1.5768 | 1.5768 | 8.6253 | 6.6004 | 4.0508 | 5.0309 | 5.4116 | 4.1412 | 2.5415 | 3.1564 | 3048.6 | 2040.8 | 1514.6 | 1078 | 33.3 | 18.2 | 24.9 | 5.3 | 1912.7294 | 1280.4232 | 950.2788 | 676.3505 | 20.8928 | 11.4189 | 15.6226 | 3.3253
4 | 2028 | 18 | 54.3869 | 8.1027 | 26.1027 | 15.4501 | 7185 | 71 | 0.998% | 4252.7905 | 42.0248 | 7.0485 | 5.0236 | 2.4739 | 3.454 | 3.372 | 1.5769 | 1.5769 | 1.5769 | 10.4204 | 6.6005 | 4.0508 | 5.0309 | 6.1678 | 3.9068 | 2.3977 | 2.9778 | 3081.2 | 2058.5 | 1539.9 | 1083.7 | 32.6 | 17.7 | 25.3 | 5.7 | 1823.7575 | 1218.423 | 911.4644 | 641.4404 | 19.2959 | 10.4766 | 14.975 | 3.3738
4 | 2029 | 18 | 82.533 | 36.2462 | 54.2462 | 30.2908 | 7256 | 71 | 0.9882% | 4051.7125 | 39.646 | 7.0485 | 5.0236 | 2.4739 | 3.454 | 31.5153 | 1.577 | 1.577 | 1.577 | 38.5638 | 6.6005 | 4.0509 | 5.031 | 21.5338 | 3.6857 | 2.262 | 2.8093 | 3115 | 2075.9 | 1564.9 | 1088.6 | 33.8 | 17.4 | 25 | 4.9 | 1739.3997 | 1159.1717 | 873.832 | 607.8686 | 18.8737 | 9.7161 | 13.9599 | 2.7361
4 | 2030 | 17.9 | 201.4793 | 142.1567 | 160.0567 | 84.3159 | 7329 | 73 | 1.006% | 3860.8258 | 38.4555 | 7.0093 | 4.9957 | 2.4602 | 3.4348 | 136.5467 | 1.87 | 1.87 | 1.87 | 143.556 | 6.8656 | 4.3302 | 5.3048 | 75.6235 | 3.6167 | 2.2811 | 2.7945 | 3147.5 | 2094.8 | 1589.9 | 1094 | 32.5 | 18.9 | 25 | 5.4 | 1658.0637 | 1103.5145 | 837.5395 | 576.3056 | 17.1206 | 9.9563 | 13.1697 | 2.8447
5 | 2031 | 18 | 129.0454 | 13.8557 | 31.8557 | 15.8313 | 7402 | 73 | 0.996% | 3678.5672 | 36.2788 | 7.0485 | 5.0236 | 2.4739 | 3.454 | 3.4639 | 3.4639 | 3.4639 | 3.4639 | 10.5124 | 8.4875 | 5.9378 | 6.9179 | 5.2243 | 4.218 | 2.9509 | 3.438 | 3181.8 | 2112.8 | 1615.5 | 1099.4 | 34.3 | 18 | 25.6 | 5.4 | 1581.2571 | 1049.9969 | 802.854 | 546.3681 | 17.046 | 8.9454 | 12.7224 | 2.6836
5 | 2032 | 17.8 | 231.7552 | 29.2597 | 47.0597 | 22.0634 | 7473 | 71 | 0.9592% | 3503.634 | 33.2876 | 6.9702 | 4.9677 | 2.4464 | 3.4156 | 6.0146 | 6.0146 | 11.216 | 6.0146 | 12.9847 | 10.9823 | 13.6624 | 9.4302 | 6.0878 | 5.1489 | 6.4055 | 4.4213 | 3214.5 | 2130.6 | 1640.7 | 1104.4 | 32.7 | 17.8 | 25.2 | 5 | 1507.083 | 998.9084 | 769.2242 | 517.7858 | 15.331 | 8.3453 | 11.8147 | 2.3442
5 | 2033 | 17.8 | 195.6715 | 57.7112 | 75.5112 | 33.3987 | 7546 | 73 | 0.9768% | 3337.6031 | 32.288 | 6.9702 | 4.9677 | 2.4464 | 3.4156 | 4.3072 | 4.3072 | 44.7895 | 4.3072 | 11.2774 | 9.275 | 47.236 | 7.7229 | 4.988 | 4.1023 | 20.8925 | 3.4158 | 3248.8 | 2148.3 | 1665.5 | 1109.2 | 34.3 | 17.7 | 24.8 | 4.8 | 1436.9474 | 950.1952 | 736.6523 | 490.6002 | 15.1709 | 7.8287 | 10.9691 | 2.123
5 | 2034 | 17.8 | 131.18 | 78.38 | 96.18 | 40.1326 | 7624 | 78 | 1.034% | 3181.2288 | 32.5467 | 6.9702 | 4.9677 | 2.4464 | 3.4156 | 1.8 | 1.8 | 72.98 | 1.8 | 8.7702 | 6.7677 | 75.4265 | 5.2156 | 3.6595 | 2.8239 | 31.4728 | 2.1763 | 3283.8 | 2166.9 | 1691.2 | 1114.9 | 35 | 18.6 | 25.7 | 5.7 | 1370.215 | 904.1717 | 705.6787 | 465.2088 | 14.6043 | 7.7611 | 10.7237 | 2.3784
5 | 2035 | 17.9 | 179.004 | 126.204 | 144.104 | 56.726 | 7696 | 72 | 0.9444% | 3029.5018 | 28.3425 | 7.0093 | 4.9957 | 2.4602 | 3.4348 | 1.8 | 1.8 | 97.4919 | 25.112 | 8.8093 | 6.7957 | 99.9521 | 28.5469 | 3.4678 | 2.6751 | 39.3458 | 11.2374 | 3318 | 2185.4 | 1716 | 1120.7 | 34.2 | 18.5 | 24.8 | 5.8 | 1306.1184 | 860.2746 | 675.497 | 441.1594 | 13.4627 | 7.2825 | 9.7624 | 2.2831
6 | 2036 | 17.9 | 5.2 | 5.2 | 23.1 | 8.5785 | 7769 | 73 | 0.9485% | 2885.1302 | 27.1096 | 7.0093 | 4.9957 | 2.4602 | 3.4348 | 0 | 5.2 | 0 | 0 | 7.0093 | 10.1957 | 2.4602 | 3.4348 | 2.603 | 3.7863 | 0.91363 | 1.2756 | 3351.9 | 2204.6 | 1741.2 | 1126.2 | 33.9 | 19.2 | 25.2 | 5.5 | 1244.7764 | 818.71 | 646.6197 | 418.2306 | 12.5893 | 7.1302 | 9.3584 | 2.0425
6 | 2037 | 17.9 | 40.5 | 40.5 | 58.4 | 20.4601 | 7846 | 77 | 0.9911% | 2748.7974 | 26.9765 | 7.0093 | 4.9957 | 2.4602 | 3.4348 | 0 | 40.5 | 0 | 0 | 7.0093 | 45.4957 | 2.4602 | 3.4348 | 2.4557 | 15.9391 | 0.86191 | 1.2034 | 3386.9 | 2222.2 | 1766.7 | 1131.4 | 35 | 17.6 | 25.5 | 5.2 | 1186.5794 | 778.534 | 618.9524 | 396.379 | 12.262 | 6.1661 | 8.9338 | 1.8218
6 | 2038 | 17.9 | 71.2 | 71.2 | 89.1 | 29.4487 | 7921 | 75 | 0.9559% | 2617.9936 | 24.7885 | 7.0093 | 4.9957 | 2.4602 | 3.4348 | 0 | 71.2 | 0 | 0 | 7.0093 | 76.1957 | 2.4602 | 3.4348 | 2.3167 | 25.1837 | 0.81312 | 1.1353 | 3420.3 | 2240.5 | 1792.4 | 1137 | 33.4 | 18.3 | 25.7 | 5.6 | 1130.4536 | 740.5144 | 592.4115 | 375.7933 | 11.0391 | 6.0484 | 8.4942 | 1.8509
6 | 2039 | 17.9 | 95.7 | 95.7 | 113.6 | 35.421 | 7996 | 75 | 0.9469% | 2493.1906 | 23.3854 | 7.0093 | 4.9957 | 2.4602 | 3.4348 | 0 | 95.7 | 0 | 0 | 7.0093 | 100.6957 | 2.4602 | 3.4348 | 2.1855 | 31.3974 | 0.7671 | 1.071 | 3456.6 | 2259.7 | 1817 | 1142.4 | 36.3 | 19.2 | 24.6 | 5.4 | 1077.7842 | 704.5851 | 566.5492 | 356.2057 | 11.3185 | 5.9867 | 7.6704 | 1.6837
6 | 2040 | 17.9 | 0 | 0 | 17.9 | 5.2654 | 8074 | 78 | 0.9755% | 2375.0107 | 22.9441 | 7.0093 | 4.9957 | 2.4602 | 3.4348 | 0 | 0 | 0 | 0 | 7.0093 | 4.9957 | 2.4602 | 3.4348 | 2.0618 | 1.4695 | 0.72368 | 1.0104 | 3490 | 2278.7 | 1842.9 | 1148.2 | 33.4 | 19 | 25.9 | 5.8 | 1026.6024 | 670.2919 | 542.099 | 337.7492 | 9.8248 | 5.589 | 7.6186 | 1.7061
7 | 2041 | 17.9 | 28 | 28 | 45.9 | 12.7375 | 8144 | 70 | 0.867% | 2260.0015 | 19.4254 | 7.0093 | 4.9957 | 2.4602 | 3.4348 | 28 | 0 | 0 | 0 | 35.0093 | 4.9957 | 2.4602 | 3.4348 | 9.7153 | 1.3863 | 0.68271 | 0.95318 | 3524.9 | 2298.4 | 1869.1 | 1153.5 | 34.9 | 19.7 | 26.2 | 5.3 | 978.1777 | 637.8177 | 518.6848 | 320.1021 | 9.6849 | 5.4669 | 7.2706 | 1.4708
7 | 2042 | 17.9 | 178 | 178 | 195.9 | 51.2861 | 8217 | 73 | 0.8964% | 2151.1881 | 19.1112 | 7.0093 | 4.9957 | 2.4602 | 3.4348 | 178 | 0 | 0 | 0 | 185.0093 | 4.9957 | 2.4602 | 3.4348 | 48.4349 | 1.3078 | 0.64407 | 0.89923 | 3558.7 | 2315.5 | 1894.8 | 1158.6 | 33.8 | 17.1 | 25.7 | 5.1 | 931.6579 | 606.1916 | 496.0535 | 303.3183 | 8.8487 | 4.4767 | 6.7282 | 1.3352
7 | 2043 | 17.9 | 134 | 134 | 151.9 | 37.516 | 8296 | 79 | 0.9614% | 2048.934 | 19.5113 | 7.0093 | 4.9957 | 2.4602 | 3.4348 | 134 | 0 | 0 | 0 | 141.0093 | 4.9957 | 2.4602 | 3.4348 | 34.8263 | 1.2338 | 0.60761 | 0.84833 | 3593.4 | 2333.7 | 1920.8 | 1164.3 | 34.7 | 18.2 | 26 | 5.7 | 887.4927 | 576.3738 | 474.3964 | 287.5571 | 8.5702 | 4.495 | 6.4214 | 1.4078
7 | 2044 | 17.9 | 0 | 0 | 17.9 | 4.1707 | 8372 | 76 | 0.9161% | 1950.6645 | 17.7079 | 7.0093 | 4.9957 | 2.4602 | 3.4348 | 0 | 0 | 0 | 0 | 7.0093 | 4.9957 | 2.4602 | 3.4348 | 1.6332 | 1.164 | 0.57322 | 0.80031 | 3629.2 | 2352.1 | 1947.4 | 1169.6 | 35.8 | 18.4 | 26.6 | 5.3 | 845.5986 | 548.0361 | 453.7415 | 272.5152 | 8.3414 | 4.2872 | 6.1978 | 1.2349
7 | 2045 | 17.9 | 0 | 0 | 17.9 | 3.9346 | 8449 | 77 | 0.9197% | 1857.1749 | 16.9254 | 7.0093 | 4.9957 | 2.4602 | 3.4348 | 0 | 0 | 0 | 0 | 7.0093 | 4.9957 | 2.4602 | 3.4348 | 1.5407 | 1.0981 | 0.54077 | 0.75501 | 3663.9 | 2370.2 | 1973.4 | 1175 | 34.7 | 18.1 | 26 | 5.4 | 805.362 | 520.9937 | 433.7731 | 258.2768 | 7.6274 | 3.9786 | 5.7151 | 1.187
8 | 2046 | 17.9 | 1.3 | 1.3 | 19.2 | 3.9815 | 8530 | 81 | 0.9587% | 1768.8486 | 16.7968 | 7.0093 | 4.9957 | 2.4602 | 3.4348 | 1.3 | 0 | 0 | 0 | 8.3093 | 4.9957 | 2.4602 | 3.4348 | 1.7231 | 1.0359 | 0.51016 | 0.71228 | 3698 | 2389.1 | 1999.6 | 1179.8 | 34.1 | 18.9 | 26.2 | 4.8 | 766.8467 | 495.4228 | 414.653 | 244.6527 | 7.0712 | 3.9193 | 5.433 | 0.99537
8 | 2047 | 17.9 | 10.125 | 10.125 | 28.025 | 5.4825 | 8607 | 77 | 0.9027% | 1683.7886 | 15.0635 | 7.0093 | 4.9957 | 2.4602 | 3.4348 | 10.125 | 0 | 0 | 0 | 17.1343 | 4.9957 | 2.4602 | 3.4348 | 3.352 | 0.9773 | 0.48129 | 0.67196 | 3731.8 | 2407.5 | 2027 | 1184.7 | 33.8 | 18.4 | 27.4 | 4.9 | 730.0526 | 470.9796 | 396.5423 | 231.763 | 6.6123 | 3.5996 | 5.3603 | 0.95859
8 | 2048 | 17.9 | 17.8 | 17.8 | 35.7 | 6.5887 | 8682 | 75 | 0.8714% | 1602.3216 | 13.8418 | 7.0093 | 4.9957 | 2.4602 | 3.4348 | 17.8 | 0 | 0 | 0 | 24.8093 | 4.9957 | 2.4602 | 3.4348 | 4.5787 | 0.92198 | 0.45404 | 0.63392 | 3768.7 | 2426 | 2053.3 | 1189.8 | 36.9 | 18.5 | 26.3 | 5.1 | 695.539 | 447.7346 | 378.9504 | 219.5856 | 6.8101 | 3.4143 | 4.8538 | 0.94124
8 | 2049 | 17.9 | 23.925 | 23.925 | 41.825 | 7.2822 | 8759 | 77 | 0.8869% | 1525.0306 | 13.4065 | 7.0093 | 4.9957 | 2.4602 | 3.4348 | 23.925 | 0 | 0 | 0 | 30.9343 | 4.9957 | 2.4602 | 3.4348 | 5.386 | 0.86979 | 0.42834 | 0.59804 | 3803 | 2445.2 | 2080.6 | 1196 | 34.3 | 19.2 | 27.3 | 6.2 | 662.1408 | 425.7341 | 362.2535 | 208.2357 | 5.972 | 3.3429 | 4.7532 | 1.0795
8 | 2050 | 17.9 | 0 | 0 | 17.9 | 2.9402 | 8837 | 78 | 0.8905% | 1451.52 | 12.8119 | 7.0093 | 4.9957 | 2.4602 | 3.4348 | 0 | 0 | 0 | 0 | 7.0093 | 4.9957 | 2.4602 | 3.4348 | 1.1513 | 0.82056 | 0.4041 | 0.56419 | 3839.1 | 2464.3 | 2107.7 | 1202.1 | 36.1 | 19.1 | 27.1 | 6.1 | 630.5908 | 404.7732 | 346.1999 | 197.4507 | 5.9296 | 3.1373 | 4.4513 | 1.002
Totals |  |  | Demand increment (MW) | Cost increment ($m) |  | Average cost ($/MW)
|  |  | 2221 | 1824.9713 |  | 821688.994
|  | PV | 947.7509 | 777.6314 |  | 820501.8357
Note on E15: John Stephenson: Not used - indicative cost of bringing a MW (at LR average incremental capital cost) forward by one year

## Major capex
RCP3 Major, Listed and other Reconductoring Capital Projects |  | Expenditure including IDC, constant 2017/18 $ | [6 empty] | Expenditure including IDC, constant 2017/18 $ | [15 empty] | Expenditure including IDC, constant 2017/18 $ | [15 empty] | Expenditure including IDC, constant 2017/18 $ | [16 empty] | Expenditure including IDC, constant 2017/18 $ | [15 empty] | Expenditure including IDC, constant 2017/18 $ | [15 empty] | Expenditure including IDC, constant 2017/18 $
|  |  |  | RCP2 | [7 empty] | RCP3 | [7 empty] | Shares | [7 empty] | RCP4 | [7 empty] | Shares | [7 empty] | RCP5 | [7 empty] | Shares | [8 empty] | RCP6 | [7 empty] | Shares | [7 empty] | RCP7 | [7 empty] | Shares | [7 empty] | RCP8 | [7 empty] | Shares
SPEND basis $m |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | RCP2 Total |  | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | RCP3 Total | E&D % | UNI | LNI | USI | LSI | UNI | LNI | USI | LSI |  | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | RCP4 Total | E&D % | UNI | LNI | USI | LSI | UNI | LNI | USI | LSI |  | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | RCP5 Total | E&D % | UNI | LNI | USI | LSI | UNI | LNI | USI | LSI |  |  | 2035/36 | 2036/37 | 2037/38 | 2038/39 | 2039/40 | RCP6] Total | E&D % | UNI | LNI | USI | LSI | UNI | LNI | USI | LSI |  | 2040/41 | 2041/42 | 2042/43 | 2043/44 | 2044/45 | RCP5 Total | E&D % | UNI | LNI | USI | LSI | UNI | LNI | USI | LSI |  | 2045/46 | 2046/47 | 2047/48 | 2048/49 | 2049/50 | RCP5 Total | E&D % | UNI | LNI | USI | LSI | UNI | LNI | USI | LSI
Approved Major Capex | Clutha - Upper Waitaki lines project | 9373826.4739 | 404807.3414 | 75720.9243 | 0 | 0 | 9854354.7396 |  | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% | bar: E&D %; Shares UNI to Shares LSI
| HVDC upgrade | 2949672.9603 | 804274.9951 | 1429793.5702 | 1758152.9414 | 0 | 6941894.4669 |  | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 5727878.3883 | 18612572.143 | 12989969.8276 | 0 | 0 | 37330420.3589 | 25% | 2333151.2724 | 2333151.2724 | 2333151.2724 | 2333151.2724 | 6.25% | 6.25% | 6.25% | 6.25% | [13 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% | [12 empty] | 0% | 0% | 0% | 0% | bar: E&D %; Shares UNI to Shares LSI
| Upper North Island dynamic reactive support (UNIDRS) | 358357.5777 | 752641.4522 | 967218.0328 | 303395.0981 | 0 | 2381612.1607 |  | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% | bar: E&D %; Shares UNI to Shares LSI
| Lower South Island reliability | 467028.7837 | 2427679.9841 | 18304455.6955 | 2092264.7062 | 0 | 23291429.1696 |  | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% | bar: E&D %; Shares UNI to Shares LSI
| Other approved projects | 5023155.8864 | 4493676.7397 | 2143357.8566 | 2107750.0003 | 2050453.6712 | 15818394.1541 |  | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% | bar: E&D %; Shares UNI to Shares LSI
Total approved aajor capital projects expenditure |  | 18172041.6819 | 8883080.5124 | 22920546.0794 | 6261562.746 | 2050453.6712 | 58287684.6909 |  | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 5727878.3883 | 18612572.143 | 12989969.8276 | 0 | 0 | 37330420.3589 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | bar: E&D %
Major capex under development | Waikato and Upper North Island voltage management | 0 | 0 | 1167262.8327 | 1902644.1179 | 602753.7484 | 3672660.6991 |  | 23025814.2805 | 65116843.9945 | 17808662.1315 | 0 | 0 | 105951320.4066 | 100% | 105951320.4066 |  |  |  | 100% | 0% | 0% | 0% |  | 0 | 0 | 1795076.1838 | 29938377.3646 | 134676732.204 | 166410185.7523 | 100% | 166410185.7523 |  |  |  | 100% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | New 220 kV line SFD-WKM (220 km) | 5200000 | 40500000 | 71200000 | 95700000 | 0 | 212600000 | 100% |  | 212600000 |  |  | 0% | 100% | 0% | 0% | OTA 220kV cable terminations | 0 | 3000000 | 3000000 | 0 | 0 | 6000000 | 100% | 6000000 |  |  |  | 100% | 0% | 0% | 0% | New 220 kV line WRK ring (56 km) | 1300000 | 10125000 | 17800000 | 23925000 | 0 | 53150000 | 100% | 53150000 |  |  |  | 100% | 0% | 0% | 0%
| South Island reliability - HVDC 2 replacement cables and 1 new cable | 0 | 0 | 0 | 0 | 0 | 0 |  | 565547.3373 | 1006937.4449 | 81896.7783 | 83689.398 | 86114.7384 | 1824185.697 | 33% | 150495.32 | 150495.32 | 150495.32 | 150495.32 | 8.25% | 8.25% | 8.25% | 8.25% |  | 87491.6787 | 89216.802 | 91862.1821 | 94580.9876 | 14302550.3012 | 14665701.9516 | 8.25% | 302480.1028 | 302480.1028 | 302480.1028 | 302480.1028 | 2.062% | 2.062% | 2.062% | 2.062% |  | 63317563.7115 | 147941206.5231 | 82199200.2041 | 0 | 0 | 293457970.4387 | 8.25% | 6052570.6403 | 6052570.6403 | 6052570.6403 | 6052570.6403 | 2.062% | 2.062% | 2.062% | 2.062% |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% | BHL-OTA 2 x 10km 220kV cables | 20000000 | 75000000 | 55000000 | 0 | 0 | 150000000 | 100% | 150000000 |  |  |  | 100% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0%
| Upper South Island voltage stability - switching station at Rangitata | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 10792164.1059 | 35086657.4438 | 24536833.9184 | 70415655.468 | 100% |  |  | 70415655.468 |  | 0% | 0% | 100% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% | BHL sub development | 8000000 | 55000000 | 34000000 | 0 | 0 | 97000000 | 100% | 97000000 |  |  |  | 100% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0%
| Upper South Island voltage stability - new line Islington | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 5201425.9708 | 40482299.9059 | 71180045.9231 | 95691913.2764 | 212555685.0762 | 100% |  |  | 212555685.0762 |  | 0% | 0% | 100% | 0% |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% | WKM sub development | 0 | 45000000 | 42000000 | 0 | 0 | 87000000 | 100% | 87000000 |  |  |  | 100% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% | bar: E&D %; Shares UNI to Shares LSI
| South Island reliability - lower South Island (Clutha - Upper Waitaki) | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 23312042 | 23312042 | 100% |  |  |  | 23312042 | 0% | 0% | 0% | 100% |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% | bar: E&D %; Shares UNI to Shares LSI
Total major capital projects expenditure under development |  | 0 | 0 | 1167262.8327 | 1902644.1179 | 602753.7484 | 3672660.6991 |  | 23591361.6179 | 66123781.4394 | 28682723.0156 | 35170346.8417 | 24622948.6568 | 178191161.5715 | [10 empty] | 87491.6787 | 89216.802 | 1886938.3659 | 30032958.3522 | 148979282.5052 | 181075887.704 | [10 empty] | 63317563.7115 | 153142632.4939 | 122681500.1101 | 71180045.9231 | 119003955.2764 | 529325697.5149 | [11 empty] | 5200000 | 40500000 | 71200000 | 95700000 | 0 | 212600000 | [10 empty] | 28000000 | 178000000 | 134000000 | 0 | 0 | 340000000 | [10 empty] | 1300000 | 10125000 | 17800000 | 23925000 | 0 | 53150000 | bar: E&D %
Listed and other reconductoring | Bunnythorpe - Haywards A and B reconductoring | 19064015.2713 | 21595825.3936 | 18429527.5705 | 14304357.8451 | 1888379.469 | 75282105.5495 |  | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% | bar: E&D %; Shares UNI to Shares LSI
| Brunswick - Stratford B reconductoring | 0 | 0 | 0 | 0 | 0 | 0 |  | 6239899.3869 | 11005033.9989 | 17794606.8813 | 11890662.1776 | 0 | 46930202.4447 | 12% | 5631624.2934 |  |  |  | 12% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0%
| Bunnythorpe - Wilton A reconductoring (BPE–JFD section) | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 4980413.9762 | 12595199.0393 | 17575613.0155 | 12% |  | 2109073.5619 |  |  | 0% | 12% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0%
| Central Park - Wilton B reconductoring | 0 | 0 | 503697.4963 | 7117753.9226 | 130755.4786 | 7752206.8975 |  | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% | bar: E&D %; Shares UNI to Shares LSI
| Oteranga Bay - Haywards A reconductoring | 0 | 0 | 0 | 2634517.1569 | 19829486.808 | 22464003.9649 |  | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% | bar: E&D %; Shares UNI to Shares LSI
| Bombay - Otahuhu A reconductoring | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 12040025.7451 | 30614901.9375 | 0 | 42654927.6826 | 0% | 0 |  |  |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0%
| Otahuhu - Whakamaru A and B reconductoring | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 28173997.5663 | 0 | 28173997.5663 | 12% | 3380879.708 |  |  |  | 12% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0%
| RCP4 and 5 reconductoring | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1 | 1 | 0 | 2 | [10 empty] | 52500000 | 52500000 | 52500000 | 52500000 | 52500000 | 262500000 | 12% | 7875000 | 7875000 | 7875000 | 7875000 | 3% | 3% | 3% | 3% |  | 60000000 | 60000000 | 60000000 | 60000000 | 60000000 | 300000000 | 12% | 9000000 | 9000000 | 9000000 | 9000000 | 3% | 3% | 3% | 3% |  |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0% | 0% | 0% | 0% | bar: E&D %; Shares UNI to Shares LSI
Total listed and other reconductoring expenditure |  | 19064015.2713 | 21595825.3936 | 18933225.0668 | 24056628.9246 | 21848621.7556 | 105498316.4118 |  | 6239899.3869 | 11005033.9989 | 29834633.6264 | 75659976.6576 | 12595199.0393 | 135334742.7091 | UNI: 115114319.7279; LNI: 2259568.8819; USI: 70566150.788; LSI: 150495.32 |  | 52500000 | 52500000 | 52500000 | 52500000 | 52500000 | 262500000 |  | 174587665.8551 | 8177480.1028 | 8177480.1028 | 8177480.1028 | [5 empty] | 60000000 | 60000000 | 60000000 | 60000000 | 60000000 | 300000000 |  | 17385721.9127 | 17385721.9127 | 229941406.9889 | 40697763.9127 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 212600000 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 340000000 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 53150000 | 0 | 0 | 0
Total Major, Listed and Other reconductoring projects |  | 37236056.9532 | 30478905.906 | 43021033.9789 | 32220835.7885 | 24501829.1751 | 167458661.8018 |  | 29831261.0048 | 77128815.4384 | 58517356.642 | 110830323.4993 | 37218147.6961 | 313525904.2806 | [10 empty] | 52587491.6787 | 52589216.802 | 54386938.3659 | 82532958.3522 | 201479282.5052 | 443575887.704 | [10 empty] | 129045442.0998 | 231755204.6369 | 195671469.9376 | 131180045.9231 | 179003955.2764 | 866656117.8738 | [11 empty] | 5200000 | 40500000 | 71200000 | 95700000 | 0 | 212600000 | [10 empty] | 28000000 | 178000000 | 134000000 | 0 | 0 | 340000000 | [10 empty] | 1300000 | 10125000 | 17800000 | 23925000 | 0 | 53150000
RCP 3 -5 peak demand-driven major capex by region
Peak-demand driven major capex | [7 empty] | Peak-demand driven major capex | 23961232.8283 | 66769737.4312 | 30763205 | 40519683.7915 | 26076675.6668 | 188090534.7177 | E&D %: UNI; UNI: 115114319.7279 | Peak-demand driven major capex | 6307218.0635 | 6307360.3862 | 8102654.8138 | 36246180.2961 | 142156692.6038 | 199120106.1633 | UNI | 174587665.8551 | [7 empty] | Peak-demand driven major capex | 13855668.6033 | 29259718.5447 | 57711226.3797 | 78380045.9231 | 126203955.2764 | 305410614.7271 | UNI | 17385721.9127 | [5 empty] | 307087707.4957 | UNI |  | Peak-demand driven major capex | 5200000 | 40500000 | 71200000 | 95700000 | 0 | 212600000 | UNI | 0 | [7 empty] | Peak-demand driven major capex | 28000000 | 178000000 | 134000000 | 0 | 0 | 340000000 | UNI | 340000000 | [7 empty] | Peak-demand driven major capex | 1300000 | 10125000 | 17800000 | 23925000 | 0 | 53150000 | UNI | 53150000
[15 empty] | E&D %: LNI; LNI: 2259568.8819 | [7 empty] | LNI |  | 8177480.1028 | [13 empty] | LNI |  | 17385721.9127 |  |  |  |  | 27822770.8973 | LNI | [8 empty] | LNI |  | 212600000 | [13 empty] | LNI |  | 0 | [13 empty] | LNI |  | 0
[15 empty] | E&D %: USI; USI: 70566150.788 | [7 empty] | USI |  |  | 8177480.1028 | [12 empty] | USI |  |  | 229941406.9889 |  |  |  | 308685037.8796 | USI | [8 empty] | USI |  |  | 0 | [12 empty] | USI |  |  | 0 | [12 empty] | USI |  |  | 0
[15 empty] | E&D %: LSI; LSI: 150495.32 | [7 empty] | LSI |  |  |  | 8177480.1028 | [11 empty] | LSI |  |  |  | 40697763.9127 |  |  | 49025739.3355 | LSI | [8 empty] | LSI |  |  |  | 0 | [11 empty] | LSI |  |  |  | 0 | [11 empty] | LSI |  |  |  | 0
[54 empty] | 692621255.6081 | Total
[15 empty] | UNI: UNI; LNI: LNI; USI: USI; LSI: LSI | [8 empty] | UNI | LNI | USI | LSI | [12 empty] | UNI | LNI | USI | LSI | [13 empty] | UNI | LNI | USI | LSI | [12 empty] | UNI | LNI | USI | LSI | [12 empty] | UNI | LNI | USI | LSI
[15 empty] | E&D %: 2020/21; UNI: 23821259.8623; LNI: 46657.6553; USI: 46657.6553; LSI: 46657.6553 | [7 empty] | 2025/26 | 1576804.5159 | 1576804.5159 | 1576804.5159 | 1576804.5159 | [11 empty] | 2030/31 | 3463917.1508 | 3463917.1508 | 3463917.1508 | 3463917.1508 | [12 empty] | 2035/36 | 0 | 5200000 | 0 | 0 | [11 empty] | 2040/41 | 28000000 | 0 | 0 | 0 | [11 empty] | 2045/46 | 1300000 | 0 | 0 | 0
[15 empty] | E&D %: 2021/22; UNI: 66520520.4136; LNI: 83072.3392; USI: 83072.3392; LSI: 83072.3392 | [7 empty] | 2026/27 | 1576840.0965 | 1576840.0965 | 1576840.0965 | 1576840.0965 | [11 empty] | 2031/32 | 6014573.1435 | 6014573.1435 | 11215999.1143 | 6014573.1435 | [12 empty] | 2036/37 | 0 | 40500000 | 0 | 0 | [11 empty] | 2041/42 | 178000000 | 0 | 0 | 0 | [11 empty] | 2046/47 | 10125000 | 0 | 0 | 0
[15 empty] | E&D %: 2022/23; UNI: 19950771.4415; LNI: 6756.4842; USI: 10798920.5901; LSI: 6756.4842 | [7 empty] | 2027/28 | 3371970.8413 | 1576894.6575 | 1576894.6575 | 1576894.6575 | [11 empty] | 2032/33 | 4307231.6184 | 4307231.6184 | 44789531.5244 | 4307231.6184 | [12 empty] | 2037/38 | 0 | 71200000 | 0 | 0 | [11 empty] | 2042/43 | 134000000 | 0 | 0 | 0 | [11 empty] | 2047/48 | 17800000 | 0 | 0 | 0
[15 empty] | E&D %: 2023/24; UNI: 4814663.5446; LNI: 604554.0525; USI: 35093561.8191; LSI: 6904.3753 | [7 empty] | 2028/29 | 31515328.0974 | 1576950.7329 | 1576950.7329 | 1576950.7329 | [11 empty] | 2033/34 | 1800000 | 1800000 | 72980045.9231 | 1800000 | [12 empty] | 2038/39 | 0 | 95700000 | 0 | 0 | [11 empty] | 2043/44 | 0 | 0 | 0 | 0 | [11 empty] | 2048/49 | 23925000 | 0 | 0 | 0
[15 empty] | E&D %: 2024/25; UNI: 7104.4659; LNI: 1518528.3506; USI: 24543938.3843; LSI: 7104.4659 | [7 empty] | 2029/30 | 136546722.3039 | 1869990.1 | 1869990.1 | 1869990.1 | [11 empty] | 2034/35 | 1800000 | 1800000 | 97491913.2764 | 25112042 | [12 empty] | 2039/40 | 0 | 0 | 0 | 0 | [11 empty] | 2044/45 | 0 | 0 | 0 | 0 | [11 empty] | 2049/50 | 0 | 0 | 0 | 0
[15 empty] | UNI: 115114319.7279; LNI: 2259568.8819; USI: 70566150.788; LSI: 150495.32 | [8 empty] | 174587665.8551 | 8177480.1028 | 8177480.1028 | 8177480.1028 | [12 empty] | 17385721.9127 | 17385721.9127 | 229941406.9889 | 40697763.9127 | [13 empty] | 0 | 212600000 | 0 | 0 | [12 empty] | 340000000 | 0 | 0 | 0 | [12 empty] | 53150000 | 0 | 0 | 0
[15 empty] | E&D %: Check; UNI: 0; LNI: 0; USI: 0; LSI: 0 | [7 empty] | Check | 0 | 0 | 0 | 0 | [11 empty] | Check | 0 | 0 | 0 | 0 | [12 empty] | Check | 0 | 0 | 0 | 0 | [11 empty] | Check | 0 | 0 | 0 | 0 | [11 empty] | Check | 0 | 0 | 0 | 0
Note on R13: Clive Bull: Voltage management capex is either generation decommissioning or demand increase, depending on how you look at it. Either way, it's a UNI benefit.
Note on BH13: Clive Bull: Based on ISL-TWZ line cost and distance
Note on BY13: Clive Bull: Data from NIGUP proposal for the 400kV development
Note on CP13: Clive Bull: Based on ISL-TWZ line costscaled to 25% based on relative distance
Note on BY14: Clive Bull: Data from NIGUP proposal for the 400kV development
Note on R15: Clive Bull: This one is mostly demand driven and a benefit to the USI
Note on BY15: Clive Bull: Data from NIGUP proposal for BHL 400kV substation
Note on BY16: Clive Bull: Data from NIGUP proposal for WKM 400kV substation
Note on R22: Clive Bull: ComCom Final Determination on Bunnythorpe-Haywards-A and B line conductor replacement Para 1.11.2 Transpower seeks approval for funding of up to $161 million (2020 prices) to complete the project. The larger conductors will increase the maximum capacity of these lines to about 112% of the current capacity providing up to 33 MVA of additional capacity. Para 1.11.3 The estimated additional capital cost of increasing the capacity is $10.5 million in 2013 prices and the present value of the expected additional benefit is $11.4 million. Transmission Planning Report 2018 Para 6.4.3.1 Bunnythorpe–Haywards–A and B line conductor replacement The existing Goat conductor is being replaced with Zebra conductor, providing a moderate increase in rating of 45–55 MVA per circuit.
Note on R23: Clive Bull: ComCom Final Determination on Bunnythorpe-Haywards-A and B line conductor replacement Para 1.11.2 Transpower seeks approval for funding of up to $161 million (2020 prices) to complete the project. The larger conductors will increase the maximum capacity of these lines to about 112% of the current capacity providing up to 33 MVA of additional capacity. Para 1.11.3 The estimated additional capital cost of increasing the capacity is $10.5 million in 2013 prices and the present value of the expected additional benefit is $11.4 million. Transmission Planning Report 2018 Para 6.4.3.1 Bunnythorpe–Haywards–A and B line conductor replacement The existing Goat conductor is being replaced with Zebra conductor, providing a moderate increase in rating of 45–55 MVA per circuit.
Note on R26: Clive Bull: BOB-OTA supplies Wiri only and capacity is not an issue, so assume no capacity increase in this case.
Note on R27: Clive Bull: ComCom Final Determination on Bunnythorpe-Haywards-A and B line conductor replacement Para 1.11.2 Transpower seeks approval for funding of up to $161 million (2020 prices) to complete the project. The larger conductors will increase the maximum capacity of these lines to about 112% of the current capacity providing up to 33 MVA of additional capacity. Para 1.11.3 The estimated additional capital cost of increasing the capacity is $10.5 million in 2013 prices and the present value of the expected additional benefit is $11.4 million. Transmission Planning Report 2018 Para 6.4.3.1 Bunnythorpe–Haywards–A and B line conductor replacement The existing Goat conductor is being replaced with Zebra conductor, providing a moderate increase in rating of 45–55 MVA per circuit.
Note on AH28: Clive Bull: ComCom Final Determination on Bunnythorpe-Haywards-A and B line conductor replacement Para 1.11.2 Transpower seeks approval for funding of up to $161 million (2020 prices) to complete the project. The larger conductors will increase the maximum capacity of these lines to about 112% of the current capacity providing up to 33 MVA of additional capacity. Para 1.11.3 The estimated additional capital cost of increasing the capacity is $10.5 million in 2013 prices and the present value of the expected additional benefit is $11.4 million. Transmission Planning Report 2018 Para 6.4.3.1 Bunnythorpe–Haywards–A and B line conductor replacement The existing Goat conductor is being replaced with Zebra conductor, providing a moderate increase in rating of 45–55 MVA per circuit.
Note on AI28: Clive Bull: Assume reconductoring is spread evenly over the 4 island regions
Note on AX28: Clive Bull: ComCom Final Determination on Bunnythorpe-Haywards-A and B line conductor replacement Para 1.11.2 Transpower seeks approval for funding of up to $161 million (2020 prices) to complete the project. The larger conductors will increase the maximum capacity of these lines to about 112% of the current capacity providing up to 33 MVA of additional capacity. Para 1.11.3 The estimated additional capital cost of increasing the capacity is $10.5 million in 2013 prices and the present value of the expected additional benefit is $11.4 million. Transmission Planning Report 2018 Para 6.4.3.1 Bunnythorpe–Haywards–A and B line conductor replacement The existing Goat conductor is being replaced with Zebra conductor, providing a moderate increase in rating of 45–55 MVA per circuit.
Note on AY28: Clive Bull: Assume reconductoring is spread evenly over the 4 island regions
Note on AZ28: Clive Bull: Assume reconductoring is spread evenly over the 4 island regions
Note on BA28: Clive Bull: Assume reconductoring is spread evenly over the 4 island regions
Note on BB28: Clive Bull: Assume reconductoring is spread evenly over the 4 island regions

## Demand
Year | RCP | NZ | NI | SI | UNI | LNI | USI | LNI | Northland | Auckland | Waikato | Bay of Plenty | Central Districts | Hawkes Bay | Taranaki | Wellington | NI | Nelson Marlborough | Canterbury | South Canterbury | West Coast | Otago Southland | SI | NZ | NI diversity | SI diversity | NZ diversity
2020 | 3 | 6616 | 4463 | 2143 | 2821.7 | 1911.6 | 1358.9 | 1037.1 | 244.2 | 1951.4 | 626.1 | 429.3 | 264.5 | 317.8 | 223.8 | 676.2 | 4733.3 | 216.7 | 832.9 | 267.5 | 41.8 | 1037.1 | 2396 | 7129.3 | 270.3 | 253 | #REF! | 6.056% | 11.81% | #REF!
2021 | 3 | 6691 | 4508 | 2161 | 2854.1 | 1929.4 | 1378.4 | 1042.8 | 246.8 | 1972.7 | 634.6 | 436.4 | 264.9 | 319.5 | 226.2 | 682.4 | 4783.5 | 220.6 | 843.2 | 272.4 | 42.2 | 1042.8 | 2421.2 | 7204.7 | 275.5 | 260.2 | #REF! | 6.111% | 12.04% | #REF!
2022 | 3 | 6759 | 4554 | 2178 | 2885.9 | 1948 | 1397.4 | 1048.6 | 249 | 1993.8 | 643.1 | 443.8 | 265.4 | 321.6 | 228.8 | 688.4 | 4833.9 | 224.4 | 852.9 | 277.6 | 42.5 | 1048.6 | 2446 | 7279.9 | 279.9 | 268 | #REF! | 6.146% | 12.3% | #REF!
2023 | 3 | 6831 | 4602 | 2196 | 2917 | 1968 | 1418.2 | 1055.3 | 251.5 | 2013.7 | 651.8 | 451.9 | 265.5 | 323.9 | 231.3 | 695.4 | 4885 | 228.4 | 864.3 | 282.8 | 42.7 | 1055.3 | 2473.5 | 7358.5 | 283 | 277.5 | #REF! | 6.15% | 12.64% | #REF!
2024 | 3 | 6901 | 4649 | 2213 | 2949.1 | 1985.9 | 1438.9 | 1061.1 | 254 | 2034.3 | 660.8 | 459.3 | 266.1 | 325.5 | 233.9 | 701.1 | 4935 | 232.3 | 875.5 | 288.1 | 43 | 1061.1 | 2500 | 7435 | 286 | 287 | #REF! | 6.152% | 12.97% | #REF!
2025 | 4 | 6972 | 4697 | 2230 | 2981.9 | 2004.1 | 1464.3 | 1066.4 | 256.5 | 2055.6 | 669.8 | 466.5 | 266.5 | 327.4 | 236.5 | 707.2 | 4986 | 236.1 | 891.7 | 293.2 | 43.3 | 1066.4 | 2530.7 | 7516.7 | 289 | 300.7 | #REF! | 6.153% | 13.48% | #REF!
2026 | 4 | 7045 | 4743 | 2247 | 3015.3 | 2022.6 | 1489.7 | 1072.7 | 259.1 | 2077.6 | 678.6 | 473.9 | 266.9 | 329.3 | 239.1 | 713.4 | 5037.9 | 240 | 907.6 | 298.5 | 43.6 | 1072.7 | 2562.4 | 7600.3 | 294.9 | 315.4 | #REF! | 6.218% | 14.04% | #REF!
2027 | 4 | 7114 | 4791 | 2265 | 3048.6 | 2040.8 | 1514.6 | 1078 | 261.7 | 2099.6 | 687.3 | 481 | 267.8 | 331.3 | 241.7 | 719 | 5089.4 | 243.9 | 923.1 | 303.7 | 43.9 | 1078 | 2592.6 | 7682 | 298.4 | 327.6 | #REF! | 6.228% | 14.46% | #REF!
2028 | 4 | 7185 | 4840 | 2281 | 3081.2 | 2058.5 | 1539.9 | 1083.7 | 264.3 | 2120.7 | 696.2 | 488.1 | 268 | 332.9 | 244.3 | 725.2 | 5139.7 | 247.9 | 938.7 | 309 | 44.3 | 1083.7 | 2623.6 | 7763.3 | 299.7 | 342.6 | #REF! | 6.192% | 15.02% | #REF!
2029 | 4 | 7256 | 4889 | 2298 | 3115 | 2075.9 | 1564.9 | 1088.6 | 267 | 2143.1 | 704.9 | 495.1 | 268.9 | 334.6 | 246.9 | 730.4 | 5190.9 | 251.8 | 954.2 | 314.3 | 44.6 | 1088.6 | 2653.5 | 7844.4 | 301.9 | 355.5 | #REF! | 6.175% | 15.47% | #REF!
2030 | 5 | 7329 | 4940 | 2315 | 3147.5 | 2094.8 | 1589.9 | 1094 | 269.6 | 2164.1 | 713.8 | 502.8 | 269.2 | 336.5 | 249.5 | 736.8 | 5242.3 | 255.8 | 969.5 | 319.7 | 44.9 | 1094 | 2683.9 | 7926.2 | 302.3 | 368.9 | #REF! | 6.119% | 15.94% | #REF!
2031 | 5 | 7402 | 4988 | 2332 | 3181.8 | 2112.8 | 1615.5 | 1099.4 | 272.2 | 2187 | 722.6 | 509.7 | 269.7 | 338.3 | 252.2 | 742.9 | 5294.6 | 259.8 | 985.3 | 325.1 | 45.3 | 1099.4 | 2714.9 | 8009.5 | 306.6 | 382.9 | #REF! | 6.147% | 16.42% | #REF!
2032 | 5 | 7473 | 5039 | 2349 | 3214.5 | 2130.6 | 1640.7 | 1104.4 | 275 | 2208.1 | 731.4 | 517 | 270.6 | 339.9 | 254.7 | 748.4 | 5345.1 | 263.7 | 1000.7 | 330.7 | 45.6 | 1104.4 | 2745.1 | 8090.2 | 306.1 | 396.1 | #REF! | 6.075% | 16.86% | #REF!
2033 | 5 | 7546 | 5089 | 2366 | 3248.8 | 2148.3 | 1665.5 | 1109.2 | 277.7 | 2230.8 | 740.3 | 523.5 | 270.9 | 342 | 257.2 | 754.7 | 5397.1 | 267.7 | 1015.8 | 336 | 46 | 1109.2 | 2774.7 | 8171.8 | 308.1 | 408.7 | #REF! | 6.054% | 17.27% | #REF!
2034 | 5 | 7624 | 5140 | 2384 | 3283.8 | 2166.9 | 1691.2 | 1114.9 | 280.4 | 2254.3 | 749.1 | 530.7 | 271.8 | 343.9 | 259.9 | 760.6 | 5450.7 | 271.7 | 1031.4 | 341.7 | 46.4 | 1114.9 | 2806.1 | 8256.8 | 310.7 | 422.1 | #REF! | 6.045% | 17.71% | #REF!
2035 | 6 | 7696 | 5190 | 2401 | 3318 | 2185.4 | 1716 | 1120.7 | 283 | 2277.1 | 757.9 | 538.2 | 272.4 | 345.5 | 262.5 | 766.8 | 5503.4 | 275.7 | 1046.5 | 347.1 | 46.7 | 1120.7 | 2836.7 | 8340.1 | 313.4 | 435.7 | #REF! | 6.039% | 18.15% | #REF!
2036 | 6 | 7769 | 5242 | 2419 | 3351.9 | 2204.6 | 1741.2 | 1126.2 | 286 | 2299.6 | 766.3 | 545.7 | 273.4 | 347.5 | 265 | 773 | 5556.5 | 279.8 | 1061.7 | 352.6 | 47.1 | 1126.2 | 2867.4 | 8423.9 | 314.5 | 448.4 | #REF! | 6% | 18.54% | #REF!
2037 | 6 | 7846 | 5294 | 2437 | 3386.9 | 2222.2 | 1766.7 | 1131.4 | 288.8 | 2323.3 | 774.8 | 552.8 | 274.1 | 349.3 | 267.6 | 778.4 | 5609.1 | 283.9 | 1077.1 | 358.3 | 47.4 | 1131.4 | 2898.1 | 8507.2 | 315.1 | 461.1 | #REF! | 5.952% | 18.92% | #REF!
2038 | 6 | 7921 | 5346 | 2455 | 3420.3 | 2240.5 | 1792.4 | 1137 | 291.6 | 2345.2 | 783.5 | 560 | 274.5 | 350.9 | 270.3 | 784.8 | 5660.8 | 287.9 | 1093 | 363.8 | 47.7 | 1137 | 2929.4 | 8590.2 | 314.8 | 474.4 | #REF! | 5.889% | 19.32% | #REF!
2039 | 6 | 7996 | 5398 | 2471 | 3456.6 | 2259.7 | 1817 | 1142.4 | 294.4 | 2370.1 | 792.1 | 567.4 | 275.4 | 352.8 | 272.8 | 791.3 | 5716.3 | 291.8 | 1107.4 | 369.6 | 48.2 | 1142.4 | 2959.4 | 8675.7 | 318.3 | 488.4 | #REF! | 5.897% | 19.77% | #REF!
2040 | 7 | 8074 | 5452 | 2490 | 3490 | 2278.7 | 1842.9 | 1148.2 | 297.2 | 2392 | 800.8 | 574.9 | 276.1 | 354.9 | 275.3 | 797.5 | 5768.7 | 296.1 | 1123 | 375.3 | 48.5 | 1148.2 | 2991.1 | 8759.8 | 316.7 | 501.1 | #REF! | 5.809% | 20.12% | #REF!
2041 | 7 | 8144 | 5506 | 2508 | 3524.9 | 2298.4 | 1869.1 | 1153.5 | 300.1 | 2415.2 | 809.6 | 583 | 276.8 | 356.7 | 277.8 | 804.1 | 5823.3 | 300.2 | 1139.1 | 380.9 | 48.9 | 1153.5 | 3022.6 | 8845.9 | 317.3 | 514.6 | #REF! | 5.763% | 20.52% | #REF!
2042 | 7 | 8217 | 5558 | 2526 | 3558.7 | 2315.5 | 1894.8 | 1158.6 | 302.8 | 2437.9 | 818 | 590.2 | 277.3 | 358.4 | 280.5 | 809.1 | 5874.2 | 304.4 | 1154.4 | 386.7 | 49.3 | 1158.6 | 3053.4 | 8927.6 | 316.2 | 527.4 | #REF! | 5.689% | 20.88% | #REF!
2043 | 7 | 8296 | 5611 | 2545 | 3593.4 | 2333.7 | 1920.8 | 1164.3 | 305.5 | 2461.2 | 826.7 | 597.3 | 278.3 | 360.2 | 283 | 814.9 | 5927.1 | 308.8 | 1169.7 | 392.6 | 49.7 | 1164.3 | 3085.1 | 9012.2 | 316.1 | 540.1 | #REF! | 5.634% | 21.22% | #REF!
2044 | 7 | 8372 | 5665 | 2563 | 3629.2 | 2352.1 | 1947.4 | 1169.6 | 308.5 | 2485.2 | 835.5 | 604.3 | 279.1 | 362 | 285.4 | 821.3 | 5981.3 | 313.1 | 1185.8 | 398.3 | 50.2 | 1169.6 | 3117 | 9098.3 | 316.3 | 554 | #REF! | 5.583% | 21.62% | #REF!
2045 | 8 | 8449 | 5717 | 2581 | 3663.9 | 2370.2 | 1973.4 | 1175 | 311.2 | 2508.3 | 844.4 | 611.2 | 280.2 | 363.7 | 287.9 | 827.2 | 6034.1 | 317.3 | 1201.4 | 404.1 | 50.6 | 1175 | 3148.4 | 9182.5 | 317.1 | 567.4 | #REF! | 5.547% | 21.98% | #REF!
2046 | 8 | 8530 | 5772 | 2600 | 3698 | 2389.1 | 1999.6 | 1179.8 | 314.1 | 2531.1 | 852.8 | 618.6 | 281.1 | 365.7 | 290.5 | 833.2 | 6087.1 | 321.7 | 1216.9 | 409.9 | 51.1 | 1179.8 | 3179.4 | 9266.5 | 315.1 | 579.4 | #REF! | 5.459% | 22.28% | #REF!
2047 | 8 | 8607 | 5826 | 2618 | 3731.8 | 2407.5 | 2027 | 1184.7 | 316.9 | 2553.5 | 861.4 | 626.3 | 282.1 | 367.5 | 292.8 | 838.8 | 6139.3 | 325.9 | 1233.5 | 416.1 | 51.5 | 1184.7 | 3211.7 | 9351 | 313.3 | 593.7 | #REF! | 5.378% | 22.68% | #REF!
2048 | 8 | 8682 | 5880 | 2636 | 3768.7 | 2426 | 2053.3 | 1189.8 | 319.7 | 2578.8 | 870.2 | 633.6 | 283 | 369.3 | 295.3 | 844.8 | 6194.7 | 330.2 | 1249.1 | 422 | 52 | 1189.8 | 3243.1 | 9437.8 | 314.7 | 607.1 | #REF! | 5.352% | 23.03% | #REF!
2049 | 8 | 8759 | 5936 | 2655 | 3803 | 2445.2 | 2080.6 | 1196 | 322.6 | 2601.8 | 878.6 | 641.3 | 284.3 | 371.4 | 297.9 | 850.3 | 6248.2 | 334.5 | 1265.5 | 428.1 | 52.5 | 1196 | 3276.6 | 9524.8 | 312.2 | 621.6 | #REF! | 5.259% | 23.41% | #REF!
2050 | 9 | 8837 | 5991 | 2673 | 3839.1 | 2464.3 | 2107.7 | 1202.1 | 325.4 | 2626.1 | 887.6 | 648.8 | 285.4 | 373.2 | 300.6 | 856.3 | 6303.4 | 338.7 | 1282.1 | 434.1 | 52.8 | 1202.1 | 3309.8 | 9613.2 | 312.4 | 636.8 | #REF! | 5.214% | 23.82% | #REF!
Data source:
Electricity Peak Demand Forecasts - Overview of our peak demand forecast methodology, Transpower, September 2016
Appendix E: Expected national and island peak demand forecast
Appendix G: Expected regional peak demand forecast
Note on D3: Clive Bull: Coincident peak demand.

## RCP 2 E&D base capex
Estimated breakdown of RCP 2 demand-driven E&D base capex across TPM pricing regions, using Commerce Commission's final decision on RCP 2 ($m)
|  | Recommended adjustment (ComCom's Final Decision) | [5 empty] | Dollar shares |  |  |  | % shares
POD reference | E&D Project | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | Adjusted Total | UNI | LNI | USI | LSI | UNI | LNI | USI | LSI |  | UNI | LNI | USI | LSI
PD30 | Otahuhu-Wiri Transmission Capacity | 2.5 | 8.7 | 3.6 | 0 | 0 | 14.8 | 14.8 |  |  |  | 100% | 0% | 0% | 0% | 2015/16 | 3.2531 | 0.87729 | 4.1169 | 0.75307
PD31 | Relieve Generation Constraints | 0 | 0 | 1.54 | 3.72 | 0.84 | 6.1 | 1.525 | 1.525 | 1.525 | 1.525 | 25% | 25% | 25% | 25% | 2016/17 | 9.432 | 8.0475 | 0.73199 | 2.8496
PD32 | Upper North Island Reactive Support 2012 - 2020 | 0 | 0 | 3.8578 | 4.1486 | 0.008457 | 8.0148 | 8.0148 |  |  |  | 100% | 0% | 0% | 0% | 2017/18 | 10.8793 | 16.5855 | 1.5516 | 5.3839
PD33 | Bus Section Fault Reliability | 0 | 0 | 3.2 | 5.4 | 2.3 | 10.9 | 2.725 | 2.725 | 2.725 | 2.725 | 25% | 25% | 25% | 25% | 2018/19 | 13.8009 | 2.5923 | 2.5923 | 2.5923
PD34 | Wellington Supply Security | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 2019/20 | 3.119 | 1.1406 | 3.6603 | 1.1406 | bar: % shares UNI to % shares LSI
PD35 | Otahuhu and Penrose Interconnection Capacity | 0 | 0 | 1.87 | 7.06 | 1.97 | 10.9 | 10.9 |  |  |  | 100% | 0% | 0% | 0% |  | 40.4844 | 29.2433 | 12.6531 | 12.7195
PD36 | Bunnythorpe Interconnection Capacity | 0.12422 | 3.0856 | 5.584 | 0 | 0 | 8.7937 |  | 8.7937 |  |  | 0% | 100% | 0% | 0%
PD37 | North Taranaki Transmission Capacity | 0 | 4.23 | 9.45 | 0 | 0 | 13.68 |  | 13.68 |  |  | 0% | 100% | 0% | 0%
PD38 | Timaru Interconnecting Transformers Capacity | 0 | 0 | 0 | 0 | 2.5198 | 2.5198 |  |  | 2.5198 |  | 0% | 0% | 100% | 0%
PD39 | Southland Reactive Power Support | 0 | 2.1177 | 3.8324 | 0 | 0 | 5.95 |  |  |  | 5.95 | 0% | 0% | 0% | 100%
PD40 | High Impact Low Probability Event Mitigation | 2.8023 | 2.878 | 1.4663 | 1.0394 | 1.0422 | 9.2281 | 2.307 | 2.307 | 2.307 | 2.307 | 25% | 25% | 25% | 25%
PD41 | Hororata and Kimberley Voltage Quality | 3.3638 | 0 | 0 | 0 | 0 | 3.3638 |  |  | 3.3638 |  | 0% | 0% | 100% | 0%
PD42 | Islington Spare Transformer Switchgear | 0 | 0 | 0 | 0 | 0 | 0 | bar: % shares UNI to % shares LSI
PD43 | Haywards Local Service Third Incomer | 0 | 0 | 0 | 0 | 0 | 0 | bar: % shares UNI to % shares LSI
PD44 | E&D Other | 0.21 | 0.05 | 0 | 0.21 | 0.38 | 0.85 | 0.2125 | 0.2125 | 0.2125 | 0.2125 | 25% | 25% | 25% | 25%
| Total | 9.0003 | 21.0612 | 34.4004 | 21.578 | 9.0604 | 95.1003 | 40.4844 | 29.2433 | 12.6531 | 12.7195 | 42.57% | 30.75% | 13.3% | 13.37%
[8 empty] | 42.57% | 30.75% | 13.3% | 13.37%
[6 empty] | per annum | 19.0201 | Dollar shares UNI: 73.32%; Dollar shares USI: 26.68%
[8 empty] | North Island |  | South Island
[10 empty] | check | 95.1003

## RCP 3 E&D base capex
Estimated breakdown of RCP 3 demand-driven E&D base capex across TPM pricing regions, using E&D base capex in RCP 3 verifier's report ($m)
Liklihood | Location | Region | Project | 2018 TPR | 2018 TPR trigger events | Primary driver | Grid need date | OAA Level | Deferred from RCP2 | RCP3 forecast |  |  | No = 0 | Load growth | Voltage | Compliance | Transmission constraint | Asset condition | System security | Security of supply |  | UNI | LNI | USI | LSI | NZ
[10 empty] | Investigate | Construct | Total
Extremely Likely | National | Statutory | Corridor Management Programme | - | Transpower seeking provisions within Resource Management Act 1991 to enable ongoing use, upgrade & future protection of Transpower assets from inappropriate development & land use under existing lines & adjacent to substations. Construction capex influenced by compliance with any revised requirements of Ministry for Environment National Policy Statement on Electricity Transmission following current review and any reforms in | Compliance | - | - | - | 5.13 | $ - | 5.13 |  |  |  | 5.13 | [5 empty] | 1.2825 | 1.2825 | 1.2825 | 1.2825 | 0
Extremely Likely | North Island | Auckland | Bombay (BOB) 220/110 kV interconnection transformer | 8.4.2.3 | During low generation in Waikato 110 kV system, power flows can exceed N-1 capacity of Otahuhu - Wiri section. Transpower implemented variable line rating on Otahuhu - Wiri Tee sections in 2015 to defer major investment. From summer 2018, other issues will constrain capacity & condition assessments show intervention needed by 2023. All leading options to address constraint & condition issues involves additional transformers as Bombay. | Load growth | 2022 | L4p | Yes | 0.15 | 8.79 | 8.94 |  | 8.94 | [7 empty] | 8.94
Extremely Likely | North Island | Auckland | Bussing Arapuni (ARA) - Bombay (BOB) circuit at Hamilton (HAM) | 8.4.2.3 | Relieve transmission constraints on Waikato & Central North Island 110 kV systems | Transmission constraint | 2025 | L5p | - | 0.13 | 1.59 | 1.72 |  |  |  |  | 1.72 |  |  |  |  | 1.72
Extremely likely | North Island | Auckland | 2nd Bombay (BOB) interconnection transformer | 8.4.2.3 | Deteriorating condition of 110 kV Bombay - Hamilton & Bombay - Otahuhu circuits. More economic to install 2nd interconnection transformer than refurbish 110 kV BOB - HAM line. All 110 kV BOB - HAM major life extension work cancelled; expected to remain in-service until 2030 then install 2nd transformer & dismantle lines. Needed to relieve transmission constraints on Waikato & Central North Island 110 kV systems. | Asset condition | 2022 | L4p | - | 0.13 | 5 | 5.13 | [5 empty] | 5.13 |  |  |  | 5.13
Extremely Likely | South Island | South Canterbury | Poor restoration time at Studholme | 18.4.2.1 | Investigate options to reduce system restoration times at Studholme following an outage of Studholme – Timaru circuit which will improve reliability at Studholme if & when Glenavy – Studholme permanent system split is implemented. | Load growth | 2022 | - | - | 0.05 | 0.5 | 0.55 |  | 0.55 | [10 empty] | 0.55
Extremely Likely | North Island | Waikato | Permanently split Arapuni (ARA) bus | 9.4.2.1 | Number of external factors contribute to overloading of existing ARA - HAM circuits. Reconductoring 110 kV ARA - HAM circuits not economically justifiable. Existing bus split at ARA done as short-term measure in 2011; additional regional geothermal generation, decommissioning of Auckland thermal generation & load growth in Auckland requires bus split to be permanent. Requires reconfiguring of 110 kV bus as a standard configuration. | Transmission constraint | 2018 | L3p | - | 0.05 | 1.5 | 1.55 |  |  |  |  | 1.55 | [5 empty] | 1.55
Extremely Likely | North Island | Waikato | Hangatiki (HTI) voltage constraints | 9.4.2.5 | Existing load constraints on Waikato 110 kV network, The Lines Company forecasting additional 56 MW load in stages over 2018-21. Load growth in regional diary industry. Currently high reactive power consumption at Hangatiki due to high load & low load power factor on transformers. Project requires installation of two 15 MVAr capacitor banks at Te Awamutu 110 kV bus | Load growth | 2021 | L3p | - | 0.02 | 3.2 | 3.25 |  | 3.25 | [8 empty] | 3.25
Extremely Likely | South Island | South Canterbury | Waikati Valley load control | 18.4.2.1 | Options to be discussed with Network Waitaki. May include special protection scheme to allow additional load on network, upgrading existing circuits, new grid exit point or shifting load. Medium to long term solution to be developed with Alpine Energy including new 220 kV grid exit point near Waihao (which would be customer initiated - based on investment decisions of local irrigation & dairy companies). | Load growth | - | None | - | 0.06 | 2.3 | 2.36 |  | 2.36 | [10 empty] | 2.36
Highly Likely | National | Grid backbone | Investigate HVDC black start possibility after an "island black" event | - | Not covered by TPR | System security | - | - | - | 0.08 | 4.5 | 4.58 | 0 | [5 empty] | 0 | [6 empty] | 0
Highly Likely | National | Grid backbone | Generation connection driven grid investments | 6.3.2.2 | Wairakei Ring connects generation on central North Island to load centres of Upper North island, Waikato & Bay of Plenty via two 220 kV transmission lines. During very high generation, capacity of circuits causes transmission constraint. TPR signals known transmission constraint issues if generation locates in number of regions including Wairakei Ring, Kaweru or Edgecumbe. Generation not expected to connect in all these locations during RCP3, therefore included indicative amount of generation driven investment needs. Grid need is uncertain & dependent on Wairakei area generation development timing. | Transmission constraint | - | None | - | 0.1 | 12.1 | 12.2 |  |  |  |  | 12.2 | [5 empty] | 12.2
Highly Likely | National | Grid backbone | Huntly - Stratford transmission constraint | 6.3.2.3 | During high generation Taranaki region, 220 kV Huntly - Stratford circuit constrains generation export. Identified incremental enhancements: a) install series reactor & special protection scheme on 110 kV Bunnythorpe - Mataroa circuit to reduce power flow; b) upgrade protection on Huntly - Stratford circuit, depending upon generation development in Taranaki region; c) investigate possible variable line ratings on 220 kV Tokaanu - Whakamaru circuits to address transmission constaints. Significant investment in generation in the Taranaki or Wellington regions or increase in HVDC north transfer will trigger possible major investments in transmission circuit thermal upgrades, reconductoring or new transmission lines (which will likely be in excess of Major Project threshold). | Transmission constraint | 2022 | None | - | 0.05 | 2 | 2.05 |  |  |  |  | 2.05 | [5 empty] | 2.05
Highly Likely | National | Grid backbone | Waikato & Upper North Island (WUNI) High Voltage management | 6.3.2.4 | Small loads cause voltage control issues in WUNI, which are currently addressed by HV line switching. Concern that switching may cause security of supply issues. Possible solution is installation of shunt reactor to increase grid capability to absorb reactive power during small load periods. Other alternatives to be investigated such as switching additional circuits out of service or seeking voltage support contracts. | Voltage | 2021 | None | - | 0.1 | 5.86 | 5.96 |  |  | 5.96 | [6 empty] | 5.96
Highly Likely | National | Grid backbone | Benmore (BEN) - Roxburgh (ROX) transmission capacity | 6.6.2.2 | Most of hydro generation in region consumed locally by Tiwai Point aluminium smelter with other major load centres including Dunedin & Invercargill. Region highly susceptible to local hydrology. Clutha - Upper Waitaki Lines Project (CUWLP) approved suite of projects to increase transmission capacity between Clutha & Waitaki Valley. 2nd tranche includes series reactor for Naseby - Roxburgh line coupled with Cromwell - Twizel thermal upgrade depending upon significant increase in generation or reduction in load in region. | Transmission constraint | 2020 | None | - | 0.1 | 10 | 10.1 |  |  |  |  | 10.1 | [7 empty] | 10.1
Highly Likely | National | Grid backbone | Aviemore - Benmore (BEN) transmission capacity | 6.6.2.2 | Most of hydro generation in region consumed locally by Tiwai Point aluminium smelter with other major load centres including Dunedin & Invercargill. Region highly susceptible to local hydrology. Clutha - Upper Waitaki Lines Project (CUWLP) approved suite of projects to increase transmission capacity between Clutha & Waitaki Valley. 2nd tranche includes special protection scheme for Aviemore - Benmore line depending upon significant increase in generation or reduction in load in region. | Transmission constraint | 2020 | None | - | 0.05 | 0.6 | 0.65 |  |  |  |  | 0.65 | [7 empty] | 0.65
Highly Likely | North Island | Auckland | Wiri - Wiri Tee capacity | 8.4.2.10 | Peak load at Wiri forecast to exceed N1 transformer capacity by 2022 & winter capacity of Wiri - Wiri Tee section from 2018. Can be managed operationally in short term. Short term options to be investigated to relieve transformer capacity issue. Long term circuit issue may be resolved by replacing line conductor. Complication in construction as line crosses motorway. | Load growth | 2019 | None | - | 0.06 | 2.5 | 2.56 |  | 2.56 | [7 empty] | 2.56
Highly Likely | North Island | Waikato | Arapuni (ARA) - Kinleith - Tarukenga transmission capacity | 9.4.2.2 | Capacity of Arapuni - Kinleith - Tarukenga circuits to supply connected loads limited by N-1 capacity of line section connecting Lichfield substation. Local generation at Arapuni & Kinleith critical to maintaining security of supply. Severely limited capacity for additional load growth on Arapuni - Kinleith - Tarukenga circuits. Timing of project dependent on load growth at Kinleith & Lichfield. Options to be investigated to meet future demand if/when step increase in load, although reconductoring circuits will be uneconomic based on past analysis. Small thermal capacity upgrade on part of a section may be justified. | Transmission constraint | ? | None | - | 0.1 | 0.5 | 0.6 |  |  |  |  | 0.6 | [5 empty] | 0.6
Highly Likely | South Island | Canterbury | Islington spare transformer switchgear | - | - | Security of supply | - | - | Yes | 0.05 | 1 | 1.05 | 0 | [6 empty] | 0 |  |  |  | 0
Highly Likely | South Island | Canterbury | Hororata (HOR) & Kimberley voltage quality & transmission capacity | 17.4.2.3 | Short-term solution relies on existing automatic voltage load shedding scheme at Hororata to manage voltage quality (post contingency) at Hororata & Kimberley substations. Medium term solution (within 5-7 years) involves installation of three banks of 9 MVAr capacitor banks at Hororata. Timing dependent on feedback from Orion & possible increases in dairy & irrigation loads in area. | Voltage | 2023 | L2p | Yes | 0.05 | 4.12 | 4.17 |  |  | 4.17 | [8 empty] | 4.17
Highly Likely | South Island | South Canterbury | Timaru region thermal capacity & voltage stability | 18.4.2.2 | Timaru area load forecast to exceed voltage stability limit by 2021. Other constraints in region to be resolved before Timaru load can exceed this limit. Timing dependent on resolving constraints with Studholme supply transformer & Temuka supply transformer & transmission constraint. Options include installation of shunt capacitors on Timaru 110 kV bus. | Load growth | 2021 | None | - | 0.2 | 3 | 3.2 |  | 3.2 | [9 empty] | 3.2
Highly Likely | South Island | South Canterbury | Timaru (TIM) 110 kV bus security & voltage collapse | 18.4.2.3 | Fault on Timaru 110 kV bus section will cause several network outages and issues, with a fault on zone C being the most significant by disconnecting neighbouring areas and causing voltage collapse in the Timaru, Ashburton and upper South Island areas. High-level options include reconfiguring Timaru 110 kV bus & install shunt capacitors have been identified for Timaru voltage support. No plans to investigate improved security of supply options as customers connected to single circuit line & Alpine Energy and Genesis have not requested a higher level of security. | System security | 2022 | None | - | 0.05 | 2 | 2.05 | [6 empty] | 2.05 |  |  |  |  | 2.05
Likely | North Island | Bay of Plenty | Kawerau (KAW) 110 kV ring bus | 10.4.2.1 10.5.4.1 10.5.5.4 | Generation export constraints exist for Kaweru 110 kV bus under high generation / low demand conditions. Transpower economic analysis suggests that risk of Kaweru transformer outage is low & with typical levels of generation & loads, special protection scheme will not operate. Kaweru T13 transformer due to riskbased condition replacement in 2019. Discussed options with stakeholders. If new generation proposals confirmed in Kawerau area, investment options will be investigated to address generation export constraints. Long-term solutions may address 110 kV & 220 kV transformer capacities through replacement and increasing thermal ratings of circuits, depending upon new generation proposals in Kaweru area. | Transmission constraint | 2019 | None | - | 0.1 | 0.7 | 0.8 |  |  |  |  | 0.8 | [5 empty] | 0.8
Likely | North Island | Auckland | Mount Roskill (ROS) 110 kV bus upgrade | 8.4.2.4 | Peak load forecast to exceed N-1 capacity of existing supply transformers in ROS substation from 2024. Trip on existing single bus section at ROS causes loss of supply on ROS 22 kV & 110 kV loads. Preferred option to upgrade ROS 110 kV bus to three sections. | Security of supply | 2021 | L3p | Yes | $ - | 4.6 | 4.6 | 0 | [6 empty] | 0 |  | 0
Likely | North Island | Auckland | Wellsford supply security | 7.4.2.1 | Peak load at Wellsford forecast to exceed N-1 capacity of supply transformers from 2019. Short term solution managed operationally within Vector network. Transpower to replace bushings of existing transformer to extend service life. Long term solution includes customer investment in installing larger transformers at Wellsford & Transpower upgrade of protection schemes & potential switchgear upgrade | Load growth | 2024 | None | - | 0.3 | 4 | 4.3 |  | 4.3 | [7 empty] | 4.3
Likely | North Island | Auckland | Henderson-Wellsford transmission capacity constraints | 7.4.2.2 | Outage on nearby circuit will cause Henderson - Wellsford section to exceed winter rating from 2025. Commissioning of new generation at Ngawha will help to defer issue towards end of forecast period. To reduce reliance on new generation, special protection scheme to be installed on HEN-WEL-MTO-MPE circuits. | Load growth | 2025 | None | - | 0.1 | 0.5 | 0.6 |  | 0.6 | [7 empty] | 0.6
Likely | South Island | South Canterbury | Black Point (BPT) single supply security | 18.4.2.4 | Fault on either 110 kV Oamaru - Black Point - Waitaki circuit or Waitaki 220/110 kV interconnection transformer will disconnect Black Point load. Existing configuration is issue for planning maintenance outages on line or transformer. Possible solution may involve closing bus-tie on Oamaru 110 kV bus with further investigation required. | Security of supply | 2019 | None | - | $ - | 0.3 | 0.3 | 0 | [6 empty] | 0 |  |  |  |  | 0
[10 empty] | 7.21 | 81.16 | 88.4 |  | 25.76 | 10.13 | 5.13 | 29.67 | 5.13 | 2.05 | 0 |  | 30.4925 | 21.7325 | 10.7025 | 14.9425 | 0
[12 empty] | Total E&D base capex | [8 empty] | Total demand-driven E&D base capex
[21 empty] | 77.87 | 39.16% | 27.91% | 13.74% | 19.19% |  | 77.87 | check
[10 empty] | Investigate | Construct | Total |  | Load growth | Voltage | Compliance | Transmission constraint | Asset condition | System security | Security of supply |  | UNI | LNI | USI | LSI | NZ
[22 empty] | 67.07% |  | 32.93%
[22 empty] | North Island |  | South Island
Note on O15: Clive Bull: System security, not growth-related, so don't count.
Note on O23: Clive Bull: System security, not growth-related, so don't count.
Note on O28: Clive Bull: GXP security, not growth-related, so don't count.
Note on O31: Clive Bull: GXP security, not growth-related, so don't count.

## RCP3-9 E&D dd-driven base capex
Estimated demand-driven E&D base capex by transmission pricing region for 2020-21 to 2049-2050 ($m)
Using E&D base capex in Transpower's RCP 3 proposal
| Year | RCP | NI ($m) | SI ($m) | NZ | Northland | Auckland | Waikato | Bay of Plenty | Central Districts | Hawkes Bay | Taranaki | Wellington | NI | Nelson Marlborough | Canterbury | South Canterbury | West Coast | Otago Southland | SI | HVDC | NZ | NI diversity | SI diversity | NZ diversity |  |  |  | RCP | NZ demand-driven E&D base capex ($m) | NI % of NZ
| 2020-21 | 3 | [20 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 3 | 15.3
| 2021-22 | 3 | [20 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 3 | 15.3
| 2022-23 | 3 | [20 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 3 | 15.3
| 2023-24 | 3 | [20 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 3 | 15.3
| 2024-25 | 4 | [20 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 3 | 17.8
| 2025-26 | 4 | [20 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 4 | 17.9
| 2026-27 | 4 | [20 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 4 | 18
| 2027-28 | 4 | [20 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 4 | 18
| 2028-29 | 4 | [18 empty] | 5.7 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 4 | 18
| 2029-30 | 5 | [18 empty] | 18.6 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 4 | 17.9
| 2030-31 | 5 | [18 empty] | 13 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 5 | 18
| 2031-32 | 5 | [20 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 5 | 17.8
| 2032-33 | 5 | [20 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 5 | 17.8
| 2033-34 | 5 | [20 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 5 | 17.8
| 2034-35 | 6 | 12.709 | 5.191 | [18 empty] | -12.709 | -5.191 | 0 | -100% | -100% | #DIV/0! | 5 | 17.9 | 71%
| 2035-36 | 6 | 12.709 | 5.191 | [18 empty] | -12.709 | -5.191 | 0 | -100% | -100% | #DIV/0! | 6 | 17.9 | 71%
| 2036-37 | 6 | 12.709 | 5.191 | [18 empty] | -12.709 | -5.191 | 0 | -100% | -100% | #DIV/0! | 6 | 17.9 | 71%
| 2037-38 | 6 | 12.709 | 5.191 | [18 empty] | -12.709 | -5.191 | 0 | -100% | -100% | #DIV/0! | 6 | 17.9 | 71%
| 2038-39 | 6 | 12.709 | 5.191 | [18 empty] | -12.709 | -5.191 | 0 | -100% | -100% | #DIV/0! | 6 | 17.9 | 71%
| 2039-40 | 7 | 12.709 | 5.191 | [18 empty] | -12.709 | -5.191 | 0 | -100% | -100% | #DIV/0! | 6 | 17.9 | 71%
| 2040-41 | 7 | 12.709 | 5.191 | [18 empty] | -12.709 | -5.191 | 0 | -100% | -100% | #DIV/0! | 7 | 17.9 | 71%
| 2041-42 | 7 | 12.709 | 5.191 | [18 empty] | -12.709 | -5.191 | 0 | -100% | -100% | #DIV/0! | 7 | 17.9 | 71%
| 2042-43 | 7 | 12.709 | 5.191 | [18 empty] | -12.709 | -5.191 | 0 | -100% | -100% | #DIV/0! | 7 | 17.9 | 71%
| 2043-44 | 7 | 12.709 | 5.191 | [18 empty] | -12.709 | -5.191 | 0 | -100% | -100% | #DIV/0! | 7 | 17.9 | 71%
| 2044-45 | 8 | 12.709 | 5.191 | [18 empty] | -12.709 | -5.191 | 0 | -100% | -100% | #DIV/0! | 7 | 17.9 | 71%
| 2045-46 | 8 | 12.709 | 5.191 | [18 empty] | -12.709 | -5.191 | 0 | -100% | -100% | #DIV/0! | 8 | 17.9 | 71%
| 2046-47 | 8 | 12.709 | 5.191 | [18 empty] | -12.709 | -5.191 | 0 | -100% | -100% | #DIV/0! | 8 | 17.9 | 71%
| 2047-48 | 8 | 12.709 | 5.191 | [18 empty] | -12.709 | -5.191 | 0 | -100% | -100% | #DIV/0! | 8 | 17.9 | 71%
| 2048-49 | 8 | 12.709 | 5.191 | [18 empty] | -12.709 | -5.191 | 0 | -100% | -100% | #DIV/0! | 8 | 17.9 | 71%
| 2049-50 | 9 | 12.709 | 5.191 | [18 empty] | -12.709 | -5.191 | 0 | -100% | -100% | #DIV/0! | 8 | 17.9 | 71%
RCP2 | 40.4844 | 29.2433 | 12.6531 | 12.7195 | 95.1003
RCP3 | 30.4925 | 21.7325 | 10.7025 | 14.9425 | 77.87
| 70.9769 | 50.9758 | 23.3556 | 27.662 | 172.9703
| 41.03% | 29.47% | 13.5% | 15.99%
| 70.5% |  | 29.5%
| North Island |  | South Island
Note on AH21: Phillip Beardmore: NZ demand-driven E&D base capex for 2035-50 estimated as the average NZ E&D base capex for RCP 4-5 set out in Transpower's RCP 3 proposal.
Note on AI21: Clive Bull: 71% is the NI % of NZ demand-driven E&D base capex based on actual and forecast demand-driven E&D base capex over RCP 2-3.
Note on F39: Phillip Beardmore: Estimated breakdown of RCP 2 demand-driven E&D base capex across TPM pricing regions, using Commerce Commission's final decision on RCP 2 ($m).
Note on F40: Phillip Beardmore: Estimated breakdown of RCP 3 demand-driven E&D base capex across TPM pricing regions, using E&D base capex in RCP 3 verifier's report ($m).